## Instructions
Instructions | Instructions
1. | In each section, complete column 'D' of the table. Use one of the following abbreviations to indicate how much effort is needed to meet the requirement:
OOB – Out of the Box: no software or code changes are required to meet requirement. The cost for out of the box functionality is included in the Offeror's proposed software cost.
SCON – Software configuration changes (no custom development) are required to meet requirement. Vendor must specify if cost for configuration is not included in the Offeror's proposed software cost.
AHAR – Additional Hardware is required to meet the requirement. Offeror must specify what hardware is included in base quote and must provide pricing for any additional hardware required to meet requirement.
CUST – Custom development is required to meet requirement. Offeror must include pricing for custom development to be completed in the Offeror's proposed timeline. If costs are included in Offeror's base proposal, Offer is to state that no additional costs are included.
NS – Not supported and cannot meet requirement.
2. | After each section, please enter any additional comments or feedback, including alternative approaches recommended if requirement in columb 'E' cannot be met.

## SYSTEM REQUIREMENTS
Attachment B - Requirements Compliance Matrix - REVISION 1 AVN RFP 24-0006 Public Address System Replacement
ID | Requirements | Requirement/Optional | Response Code | Description | Response Dropdown List
| SYSTEM REQUIREMENTS - HEADEND |  |  |  | OOB
3.7.A.1.a. | System headend(s) shall manage the entire PAS ecosystem. | Requirement | SCON |  | SCON
3.7.A.1.b. | System headend and components shall use but not be limited to one or multiple of the following protocols: Audinate Dante, QSC QLAN, Audio Engineering Society (AES 67). | Requirement |  |  | AHAR
3.7.A.1.c. | System Headend shall allow any authorized microphone to page any single zone, group of zones and all zones at once, across the entire system. | Requirement |  |  | CUST
3.7.A.1.d. | The headend shall have the ability to support the functions and management of the system for this project and future expansion to include but not limited to gates, concourses, curbs, and new or existing facilities. | Requirement |  |  | NS
3.7.A.1.e. | The headend shall reside on the City network and must be virtualized to the greatest extent possible utilizing VMWare and reside within the airport datacenter environment. | Requirement
3.7.A.1.f. | All servers shall be Windows Server 2022 R2, no more than (n-1), with all currently available security patches and updates. Virtualized servers do not need license provisioning. | Requirement
3.7.A.1.g. | Physical Server Requirements: | Requirement
3.7.A.1.h. | Database Software: | Requirement
3.7.A.1.i. | System shall support multiple user profiles/level with unique permissions using Role Based Access Control (RBAC) through active directory. | Requirement
3.7.A.1.j. | Headend shall support Cisco VOIP protocols for limited paging use. | Requirement
3.7.A.1.k. | Headend controllers shall provide automatic redundancy for the operation of the system. System shall be available in the event of a system controller or main components failure by automatically switching to a redundant unit with the proper settings and configurations already in place. | Requirement
3.7.A.1.l. | System shall be capable of handling over 20 priority levels for announcements, events, and pages. | Requirement
3.7.A.1.m. | System Servers (application and database) shall be fault tolerant and fault resistant. Servers should have hot swappable redundant power supplies where applicable or available. | Requirement
3.7.A.1.n. | System components shall have redundant ethernet port where applicable. | Requirement
3.7.A.1.o. | The system shall have the ability to access the backup of all content and configurations for system recovery through the network. | Requirement
3.7.A.1.p. | For all portions of the system that service T3 and T4S1, these portions of the system shall have uninterruptible power supplies (UPS) sufficient to run on UPS power to play audio from amplifiers for the Emergency Communication System (ECS) areas until the generator power fails over and comes online. Additional UPSs may be required to protect sensitive electronics. Whole room UPS covered spaces where PAS equipment resides would not require UPS. UPS shall be network enabled for health monitoring purposes. | Requirement
3.7.A.1.q. | The system shall be compatible with Veeam products for backup and restore. | Requirement
SYSTEM REQUIREMENTS - VOIP INTERFACE
3.7.A.2.a. | System shall be capable of interfacing to VOIP telephone system for convenience paging. | Requirement
3.7.A.2.b. | System shall support SIP and PBX trunking as well as standard 3rd party FXO gateways that utilize VoIP codec standards. | Requirement
SYSTEM REQUIREMENTS - PAGING STATIONS
3.7.A.3.a. | Paging stations shall be IP-based and shall be a combination of full-function and 4-button stations. | Requirement
3.7.A.3.b. | Paging stations shall have limiter compressor to provide consistent audio from the microphone. Microphones shall be a condenser type and not a dynamic type of microphone. | Requirement
3.7.A.3.c. | For overlapping page requests of the same priority into a zone, the system shall record a message and schedule it to be played immediately following the current message. | Requirement
3.7.A.3.d. | Paging station shall allow users to log into the system based on their roles to access their airline or entities profiles of zones, features and messages. | Requirement
3.7.A.3.e. | Paging Stations shall support zone and zone group selection. | Requirement
3.7.A.3.f. | Paging station shall operate two gates from one check in counter for automatic loading and announcements. | Requirement
3.7.A.3.g. | Paging stations shall be capable of providing: • Live Paging • Recorded Paging • Automated Boarding Sequence Messaging (Full Function Paging Station) | Requirement
3.7.A.3.h. | To eliminate the need for POE injectors, the paging stations need to be able to negotiate appropriate power levels with the switch via IEEE 802.3 af/at standards, Link Layer Discovery Protocol (LLDP), or Cisco Discover Protocol (CDP). | Requirement
3.7.A.3.i. | Station shall include a secondary IEEE 803.af ethernet port for redundant network and power capability. | Requirement
3.7.A.3.j. | Stations shall have desktop, surface, and flush mounting options available. | Requirement
3.7.A.3.k. | Stations shall provide internal fault status through the network connection. | Requirement
3.7.A.3.l. | Stations shall use a handheld microphone with a metal magnet landing area for ease of positioning the microphone between uses. | Requirement
3.7.A.3.m. | 4-button stations shall have indicators for power, busy and ready states, as well as an audible signal device to alert the operator to the status of the Microphone Station while in operation. | Requirement
3.7.A.3.n. | Paging station shall be capable of cancelling an announcement. | Requirement
SYSTEM REQUIREMENTS - ANCILLARY DEVICES
3.7.A.4.a. | System shall have analog input and output devices for accepting analog audio. | Requirement
3.7.A.4.b. | System shall have I/O devices for accepting or generating contact closures and I/O triggers for interfacing to other systems. | Requirement
SYSTEM REQUIREMENTS - SPEAKERS
3.7.A.5.a. | Speakers should not be placed directly overhead of the following locations: • TSA Podiums • Police Podiums • Information Desk • Gate Counters • Gate Podiums • Check-in Counters • Compassion Corner and Sensory Room | Requirement
3.7.A.5.b. | The system shall be capable of operating consistently at 15 decibels (dB) above ambient sound levels or 95dBA peak on axis to the loudspeaker. Final levels shall be set in each zone and tested with the Ambient Noise system activated. | Requirement
3.7.A.5.c. | Speech Transmission Index of 0.50 is required as the basis of design. The intent is to meet this basic intelligibility level in the typical public areas and traffic areas of the airport, understanding that there are small areas that will not pass the requirement. Speaker density and layout as well as use of line arrays and other speaker patterns shall be required during the design. The system shall be comprised of professional grade audio equipment supported by rugged, affordable, and innovative hardware that is intended for use 24 hours a day, 7 days per week. | Requirement
3.7.A.5.d. | Design is not limited to a certain speaker brand or type but a consistent approach of products for maintenance and service is required. | Requirement
3.7.A.5.e. | Per INF 200.215, J hooks are not allowed to support cabling inside buildings. All low voltage cabling must be in conduit. Reference Exhibit H - INF 200.215 Telecommunications Cabling Systems and Exhibit J - AR 1.73 Control of Communication Services and Systems. | Requirement
SYSTEM REQUIREMENTS - AMBIENT MICROPHONES
3.7.A.6.a. | The system shall provide ambient microphones to automatically adjust the level in the speaker zones. | Requirement
3.7.A.6.b. | The system shall allow multiple audio adjustments as well as automatic operation of the Ambient Noise Sensor circuitry. | Requirement
3.7.A.6.c. | The speaker zone may consist of more than one amplifier circuit so the ambient noise system shall be capable of controlling multiple circuits. | Requirement
3.7.A.6.d. | The system shall allow at least 2 ambient noise sensors to control one zone. | Requirement
3.7.A.6.e. | The system shall provide the ability to report the noise levels of each zone at pre-determined times of day. | Requirement
3.7.A.6.f. | The system shall provide the ability to schedule the times of day that the system shall record the noise levels of each zone. | Requirement
3.7.A.6.g. | The system shall provide the ability to report the noise levels upon request of authorized users at any time of day. | Requirement
3.7.A.6.h. | The system shall use the Ambient Noise Sensors to determine the noise levels of each zone. | Requirement
3.7.A.6.i. | The system shall be capable to storing the noise levels captured for future or further analysis by authorized users. | Requirement
3.7.A.6.j. | The system shall be capable of showing the peaks and low points of the noise levels throughout each day, per zone. | Requirement
SYSTEM REQUIREMENTS - ANNOUNCEMENT ZONES
3.7.A.7.a. | The system shall be able to configure any amplifier circuit or line level / network fed loudspeaker into a zone or part of a zone group. | Requirement
3.7.A.7.b. | The system shall have the ability to mute zones during press or other special events while still allowing emergency level announcements or messages to override this function. | Requirement
3.7.A.7.c. | The system shall provide the ability for multiple announcement zones to be active at the same time in each terminal with different announcements. | Requirement
SYSTEM REQUIREMENTS - PAGING AND VISUAL MESSAGING
3.7.A.8.a. | System shall provide a turnkey method and hardware to support this function. The paging station shall seamlessly integrate with this solution. | Requirement
3.7.A.8.b. | System shall provide software to manage and log passenger paging requests. System shall allow live page audio as well as text to speech paging with text to be displayed into the public areas as required. | Requirement
3.7.A.8.c. | The system shall provide a graphical user interface (GUI) for aviation personnel to submit text to speech pages. The integral time between pages and play counts shall be adjustable with a default of 3 times, 3 minutes apart. | Requirement
3.7.A.8.d. | Announcement GUI shall provide simplified operations for Command Center staff to select and play out messages and live pages. | Requirement
3.7.A.8.e. | The system shall provide an API to generate visual messages to selected information displays the existing Flight Information Display system to accompany an audible message simultaneously as a means to provide a reasonable accommodation for hearing impaired. | Requirement
3.7.A.8.f. | The Announcement GUI shall allow selection of areas and zones graphically as well as messages as required. | Requirement
3.7.A.8.g. | All functions shall operate from this software including whether the page is audio only, audio and visual, or multiple standard languages. | Requirement
3.7.A.8.h. | Requests shall be vetted through Aviation Department staff before being played in the system. | Requirement
3.7.A.8.i. | System shall support multiple user profiles/level with unique permissions using Role Based Access Control through active directory. | Requirement
SYSTEM REQUIREMENTS - MESSAGING TYPES
3.7.A.9.a. | System shall provide for the following message types: i. scheduled messages ii. data driven messages that fill in the blank of the message automatically for flight announcements iii. multiple language messages to be determined during design iv. visual text of the messages for use in with the existing Flight Information Display system v. visual paging | Requirement
3.7.A.9.b. | If speech-to-text functionality can be provided, the Contractor shall provide as an optional item on Attachment A - Fee Schedule. This option would allow recorded audio files to be translated into words that would be searchable. | Requirement
3.7.A.9.c. | The system shall support audio files as scheduled messages. The system shall be capable of importing audio files into the system for mayor messages or special events as required. | Requirement
3.7.A.9.d. | The system shall support data driven sequences like bags coming up on baggage claim carousel. | Requirement
3.7.A.9.e. | The system shall have automated pre-boarding and boarding airline message library to streamline boarding processes. | Requirement
3.7.A.9.f. | The system shall have text-to-speech software. This shall support the Command Center text-to-audio for integration with visual paging. | Requirement
3.7.A.9.g. | The system shall queue live announcements for competing microphone stations in conjunction with the messages being played in the zone according to priority levels. | Requirement
SYSTEM REQUIREMENTS - INTEGRATIONS
3.7.A.10.a. | The Contractor shall provide a manufacturer's list of the common APIs that their system is compatible with in the airport vertical market. | Requirement
3.7.A.10.b. | The system shall be integrated with the fire alarm system to have the capability of shunting or muting during a fire alarm event. | Requirement
3.7.A.10.c. | The system shall be capable of overriding existing messages and giving priority to the FACP audio in newer areas of Terminal 3 and Terminal 4. | Requirement
3.7.A.10.d. | The system shall provide an API for integration to the Flight Information Display Systems (FIDS) for visual paging. | Requirement
3.7.A.10.e. | The system shall integrate with Baggage Input Consoles SITA’s Airport Integrator for paging in baggage claim. | Requirement
3.7.A.10.f. | The system shall provide emergency messaging. | Requirement
3.7.A.10.g. | The system shall integrate with the FACP in T3 and T4S1. | Requirement
3.7.A.10.i. | The system shall integrate with the existing T3 and T4S1 components to provide SCADA Monitoring. | Requirement
3.7.A.10.j. | The Contractor shall provide an integration of the PAS into the Sky Train ECS at the station platforms. Specifications for existing Sky Train ECS are outlined in the Confidential Drawings. See Paragraph Z. Confidential Drawings, on pg. 26 herein for further instructions. | Requirement
3.7.A.10.k. | The system shall integrate with the existing Hearing Loop System within the gate hold areas in T3 and T4S1. | Requirement
3.7.A.10.l. | The system shall integrate with the following named systems: | Requirement
SYSTEM REQUIREMENTS - PERFORMANCE REQUIREMENTS
3.7.A.11.a. | System Availability shall be measured over a rolling 12-month period. | Requirement
3.7.A.11.b. | Redundant hardware components are required to prevent outages related to hardware component failures. These must include dual socket/dual CPU, dual power supplies. | Requirement
3.7.A.11.c. | Offeror shall propose method to provide for high availability, fault tolerance, and/or failover to ensure system availability in the event of a significant server hardware failure. Microsoft Clustering is not an approved method of achieving this requirement. | Requirement
SYSTEM REQUIREMENTS - MONITORING AND TESTING SYSTEM
3.7.A.12.a. | System shall have fault monitoring, reporting, alerts, and logging. | Requirement
3.7.A.12.b. | System shall be capable of providing logging for a minimum of 90 days, dependent on storage requirements of database server where log files reside. Logging should solely be based on storage of log files not limited by the application. | Requirement
3.7.A.12.c. | System shall provide end to end testing of all signals and equipment health status including end of line status and ground faults. This information shall be presented on a GUI dashboard for Aviation Department staff to monitor. | Requirement
3.7.A.12.d. | System shall generate an automatic fault report in real time as the system monitors and automatically tests itself to the greatest extent possible. | Requirement
3.7.A.12.e. | System shall have announcement logging providing the following types of information for messages: • Message ID • Scheduled Time • Actual Time Played • Duration • Priority • Zone • Repeat Interval • Repeat Count • Text (for Text to Speech (TTS) and pre-recorded messages) • Path (filename of saved output WAV file) | Requirement
3.7.A.12.f. | System shall have announcement logging providing the following types of information for microphone usage: • Live ID • Start Time • Duration • Paging Station • Microphone • Priority • Zone • Logged in User • Is Record Only • Status • Path (filename of saved output WAV file) | Requirement
3.7.A.12.g. | The PAS shall supervise all associated endpoint devices, report system events, and log faults to be reported via SNMP, email, and SMS via email notifications. | Requirement
3.7.A.12.h. | Forensic level reporting for diagnostics reviews of what is being announced when, from where, and by whom when an anomaly has occurred. | Requirement
3.7.A.12.i. | System shall have device discovery and logical architecture of the system layout. | Requirement
SYSTEM REQUIREMENTS - AMPLIFIERS
3.7.A.13.a. | Amplifiers shall be loaded to 80% capacity maximum, per channel. | Requirement
3.7.A.13.b. | Amplifiers shall be standardized around select models and channel capacity for ease of maintenance and service. | Requirement
3.7.A.13.c. | Amplifiers shall be multichannel 70-volt rack mountable units. | Requirement
3.7.A.13.d. | Amplifiers shall have a seamless smart backup amplifier schema at a ratio of 4:1. | Requirement
3.7.A.13.e. | Amplifiers shall have both analog and network/digital audio inputs matching the manufacturers system requirements. | Requirement
3.7.A.13.f. | Amplifiers shall have report impedance measurements and ground faults of the speaker circuits. | Requirement
3.7.A.13.g. | Amplifiers or software shall report End of line status on the speaker circuits. | Requirement

## Data Validation (hidden)
Compliance Response
Out of the Box
Configuration Change
Programming Change - On Roadmap
Programming Change - Custom Development
Not Supported